SECTION 05501

ANCHOR BOLTS

PART 1 - GENERAL

1-01	DESCRIPTION:

A. 	This section specifies anchor bolts complete with washers and nuts.  Unless otherwise specified, anchor bolts shall be hot-dip galvanized or type 304 stainless steel.

1-02	REFERENCES:

A.	This section contains references to the following documents.  They are a part of this section as specified and modified.  In case of conflict between the requirements of this section and those of the listed documents, the requirements of this section shall prevail.

Reference				Title

ASTM A36/A36M-00a		Structural Steel

ASTM A307-00			Carbon Steel Bolts and Studs, 60,000 psi Tensile Strength

ASTM A320/A320M-00b		Alloy-Steel Bolting Materials for Low Temperature Service

IBC 2009				International Building Code

PART 2 - 	PRODUCTS

2-01	GENERAL:

A. 	Anchor bolt holes in beam supports and other shall not exceed the bolt diameters by more than 25 percent, up to a limiting maximum oversizing of l/4 inch.  Unless otherwise specified, minimum anchor bolt diameter shall be 5/8 inch. Tapered washers shall be provided where mating surface is not parallel or square with the nut.

B. 	Expansion, wedge, or adhesive anchors set in holes drilled in the concrete after the concrete is placed will not be permitted in substitution for anchor bolts except where otherwise specified.  Upset threads shall not be acceptable.

2-02	MATERIALS:

A.	Anchor bolt materials shall be as specified in Table A.

| TABLE A ANCHOR BOLT MATERIALS |  |
| --- | --- |
| MATERIAL | SPECIFICATION |
| Steel bolts | ASTM A307, Grade A |
| Fabricated steel bolts | ASTM A36 |
| Stainless steel bolts, nuts, washers | ASTM A320, Type 304a |
| Expansion anchors | HILTI-BOLT, McCulloch Industries, or equal |
| Wedge anchors | ITT, Phillips Drill Co., or equal. |
| Chemical anchors (Use a Type 304 where specified) | Hilti -HAS-R Threaded Rods; Hilti HIT-HY100 |

2-03	DESIGN:

A.	Anchor bolts for equipment frames and foundations shall be designed in accordance with the IBC.

2-04	PRODUCT DATA:

A.	The following information shall be provided for all bolt systems not cast-in-place:

1. 	Data indicating load capacities.

2. 	Chemical resistance.

3. 	Temperature limitations.

4. 	Installation instructions.

PART 3 - EXECUTION

3-01	GENERAL:

- Fieldwork, including cutting and threading, shall not be permitted on galvanized items.  Dissimilar metals shall be protected from galvanic corrosion by means of pressure tapes, coatings or isolators.

3-02	CAST-IN-PLACE ANCHOR BOLTS:

A.	Anchor bolts to be embedded in concrete shall be placed accurately and held in correct position while the concrete is placed or, if specified, recesses or blockouts shall be formed in the concrete and the metalwork shall be grouted in place in accordance with Section 03300.  The surfaces of metalwork in contact with concrete shall be thoroughly cleaned.

B. 	After anchor bolts have been embedded, their threads shall be protected by grease and the nuts run on.

3-03	ADHESIVE ANCHOR BOLTS:

A.	Use of adhesive or capsule anchors shall be approved by Engineer and subject to the following conditions:

1. 	Use shall be limited to locations where exposure, on an intermittent or continuous basis, to acid concentrations higher than 10 percent, to chlorine gas, or to machine or diesel oils, is extremely unlikely.

2. 	Use shall be limited to applications where exposure to fire or exposure to concrete or rod temperature above 120 degrees F is extremely unlikely.

3. 	Approval from Construction Manager for specific application and from supplier of equipment to be anchored, if applicable.

4. 	Anchor diameter and grade of steel shall be per contract documents or per equipment supplier specifications.  Anchor shall be threaded or deformed full length of embedment and shall be free of rust, scale, grease, and oils.

5. 	Embedment depth shall be as specified.  Adhesive capsules of different diameters may be used to obtain proper volume for the embedment, but no more than two capsules per anchor may be used.  When installing different diameter capsules in the same hole, the larger diameter capsule shall be installed first.  Any extension or protrusion of the capsule from the hole is prohibited.

6. 	All installation recommendations by the anchor system manufacturer shall be followed carefully, including maximum hole diameter.

7. 	Holes shall have rough surfaces, such as can be achieved using a rotary percussion drill.

8. 	Holes shall be blown clean with compressed air and be free of dust or standing water prior to installation.

9. 	Anchor shall be left undisturbed and unloaded for full adhesive curing period.

10. 	Concrete temperature (not air temperature) shall be compatible with curing requirements of adhesives per adhesive manufacturer.  Anchors shall not be placed in concrete below 25 degrees.

3-04	EXPANSION ANCHORS:

A.	Use of expansion or wedge type anchors shall be subject to conditions 2, 3, 4, 6, 7, and 8 specified in Paragraph 05501-3.03.

B.	The Contractor shall supply the Construction Inspector with the current evaluation report from the International Conference of Building Officials for the particular brand of expansion anchors to be used

PART 4- MEASUREMENT AND PAYMENT

4-01	MEASUREMENT AND PAYMENT

There will be no direct measurement for installation of ANCHOR BOLTS. Payment for this work shall be included as an indirect cost to the associated bid items where bolt installation work is performed.

***END OF SECTION***