# SECTION 16010

ELECTRICAL GENERAL PROVISIONS

# PART 1 - GENERAL

1.01	RELATED DOCUMENTS: The general provisions of the Contract, including General and Special Provisions, and Division 1 - General.  Sections included in the DIVISION 16 Specifications are as follows:

SUB-SECTION 16010 - ELECTRICAL GENERAL PROVISIONS

SUB-SECTION 16111 - RACEWAYS

SUB-SECTION 16120 - WIRES AND CABLES

SUB-SECTION 16135 - ELECTRICAL BOXES AND FITTINGS

SUB-SECTION 16140 - WIRING DEVICES

SUB-SECTION 16181 - OVERCURRENT PROTECTIVE DEVICES

SUB-SECTION 16190 - SUPPORTING DEVICES

SUB-SECTION 16195 - ELECTRICAL IDENTIFICATION

SUB-SECTION 16441 - ENCLOSED SWITCHES

SUB-SECTION 16450 - GROUNDING

SUB-SECTION 16510 - LIGHTING

SUB-SECTION 16902 - ELECTRICAL CONTROLS AND RELAYS

1.02	DESCRIPTION OF WORK:

A.	This Section specifies several categories of provisions for electrical work, including:  (1) Certain adaptive expansions of requirements specified in DIVISION 1, (2) General performance requirements within the electrical systems as a whole, and (3) General work to be performed as electrical work because of its close association.

B.	These Specifications and accompanying Drawings are intended to describe complete workable systems of the various types.  Items of materials, work, or equipment not mentioned but normally necessary for the proper execution of this work, shall be provided as if specifically called for, at no additional cost to the Owner.

C.	Where these specifications and associated drawings appear to conflict, consult engineer for resolution.  For bid purposes, Contractor shall interpret the documents in the manner which has the largest cost impact to the project.

1.03	SUMMARY OF ELECTRICAL WORK:

A.	Drawings:  Refer to the Electrical Drawings for graphic representations, schedules and notations showing electrical work.

1.	The Drawings show approximate locations only of feeders, branch circuits, outlets, etc., except where specific routing or dimensions are indicated.  The Engineer reserves the right to make reasonable changes in locations indicated before roughing in without additional cost to the Owner.

2.	Because of the small scale of the Drawings, it is not possible to indicate all of the offsets, fittings, and accessories required.  The Contractor shall investigate the structural and finish conditions affecting his work and shall arrange such work accordingly, furnishing fittings, bends, junction boxes, pull boxes, access panels, and accessories required to meet such conditions.

B.	Specifications:

1.	Refer to the DIVISION 16 sections for the primary technical specifications of electrical work.

2.	General Outline:  This section of the specifications covers furnishing materials, equipment, constant competent supervision, special tools, test equipment, technicians, and labor necessary for installation of a complete working electrical system, all as indicated on the plans and in these Specifications.

C. 	Scope:

1.	Under this part of the contract, electrical facilities will be constructed as indicated on the plans, and in these Specifications.

2.	The work shall include, but not necessarily be limited to, furnishing and installing the following:

- Furnish and install all electrical equipment, components, devices, fixtures, and systems as illustrated on the drawings for the Marvin Braud Pump Station Flood Prtection Improvements project.

d.	Furnish and install and connect power distribution systems - feeder & branch circuits/panels/wiring/receptacles/devices/etc.

e.	Furnish and install and connect power wiring as required to all mechanical equipment, including the raceway system and outlet boxes for associated control wiring.

f.	Furnish and install raceway systems.

g.	Provide drawings for all new and revised work. Provide O & M documentation on all work performed.

1.04	COORDINATION OF ELECTRICAL WORK:

A.	General:  Refer to the DIVISION 1 sections for general coordination requirements applicable to the entire work.  It is recognized that the contract documents are diagrammatic in showing certain physical relationships, which must be established within the electrical work, and in its interface with other work including utilities and mechanical work, and that such establishment is the exclusive responsibility of the Contractor.

B.	Arrange electrical work in a neat, well-organized manner with exposed conduit and similar services running parallel with primary lines of the building construction.

C.	Submit coordination drawings prior to purchase-fabrication-installation of any of the elements involved in the construction.

D.	Verify final locations for rough-ins with field measurements and with the manufacturer drawings detail requirements of the actual equipment to be connected.

E.	Verify all dimensions by field measurements.

F.	Arrange for sleeves, slots, and openings in other building components to allow for electrical installations.

G.	Coordinate the installation of required supporting devices and sleeves to be set in poured in place concrete and other structural components, as they are constructed.

H.	Sequence, coordinate and integrate installations of electrical materials and equipment for efficient flow of the work.

I.	Coordinate the cutting and patching of building components to accommodate the installation of electrical equipment and materials.

J.	Where mounting heights are not detailed or dimensioned, install electrical services and overhead equipment services and overhead equipment to provide the maximum headroom possible.

K.	Install electrical equipment to facilitate maintenance and repair or replacement of equipment for ease of disconnecting, with minimum of interference with other installations.

L.	Install equipment and components so that they do not obstruct station operations or impede upon required clearances for safety or equipment access.  In particular, new conduits shall be routed so that they do not impede new crane operations.

M.	Coordinate rough-ins and electrical installations supporting new equipment with new equipment supplier, prior to rough-ins.  In particular, coordinate disconnect switch location and power connection requirements with crane supplier and gate actuator supplier.  Furthermore, coordinate locations of starters and panels with station operators prior to rough-in.

1.05	TEMPORARY ELECTRICITY:

A.	Contractor shall arrange and install temporary electric construction power, including paying for any utility service charge for said temporary service, according to utility service standards and the requirements of the Contractor.  All 120-volt receptacles used for construction power shall be protected by ground fault interrupter (GFI) devices.  Provide temporary lighting during construction as required.  All temporary lighting shall meet OSHA safety requirements.  All temporary equipment and work shall comply with NFPA-70 (NEC).

1.06	TEMPORARY USE OF PERMANENT EQUIPMENT

A.	The contractor shall not use the permanent equipment and systems installed on this project for temporary construction purposes without the express written permission from the Engineer.

B.	The acceptable temporary use of the permanently installed equipment, electrical distribution system or other type systems are as follows:

1.	Temporary energizing equipment or system, according to manufacturer’s instructions, for testing, adjusting and/or demonstrating for inspections.

2.	Temporary energizing motorized equipment, associated starter and controls, according to manufacturer’s instructions, for the purpose of testing, adjusting controls, systems balance and/or temperature regulation.

3.	Temporary energizing motor winding or electronic panel heaters, according to manufacturer’s instructions, to prevent the accumulation of moisture.

1.07	QUALITY ASSURANCE, STANDARDS:

A.	General:  In addition to standards specified in individual work sections, the following standards are imposed, as applicable to the work in each instance:

NFPA 70, National Electrical Code (NEC)

NFPA 70E, Standard for Electrical Safety Requirements for Employee Workplaces

NEMA/ANSI/ASTM

Electrical material shall be built and tested in accordance with the applicable standards of the National Electrical Manufacturer’s Association (NEMA); the American National Standards Institute (ANSI); and the American Society of Testing and Materials (ASTM).

Underwriters’ Laboratories (UL)

Electrical materials shall be new and unused and shall be listed, inspected, approved and labeled by Underwriters’ Laboratories, Inc., where such labeling service is available.

NFPA-101, Life Safety Code

OSHA Code of Federal Regulations (for construction practices)

OSHA 29.CFR1910.  Subpart 3

NECA 1 – 2000, Standard Practices for Good Workmanship in Electrical Contracting

All applicable state and local codes/ordinances.

B.	Manufacturers:  Only firms regularly engaged in manufacture of electrical products of types required, whose products have been in satisfactory use in similar service for not less than 3 years, shall be utilized.

1.08	ELECTRICAL SUBMITTALS:

A.	Refer to the Conditions of the Contract (General and Supplementary) and Division 1 Section:  SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES for submittal definitions, requirements, and procedures.

B.	Submittal of shop drawings, product data, and samples will be accepted only when submitted by the Contractor and received by the Engineer, during normal business hours, not later than eight (8) working days prior to date of bid.  Data submitted from subcontractors and material suppliers directly to the Engineer will not be processed.

C.	ELECTRICAL SUBMITTALS:  Submit to the Engineer for review and general compliance, complete descriptive and dimensional data on the following materials, which Contractor proposes to use.  (Comply with Section 01300).

- Conduit and fittings.

- Circuit breakers.

- Wiring devices.

- Devices and covers.

- Conductors.

- Wire markers.

- Controls

- Grounding system components.

- Light fixtures

- Panelboards

D.	Corrections or comments made on shop drawings during the review do not relieve the Contractor from compliance with requirements of the Contract Documents, Plans and Specifications.  Shop drawings will be checked for general conformance with the design concept of the project and general compliance with information given in the contract documents.  Review of shop drawings shall not relieve the Contractor from responsibility for confirming and correlating all quantities and dimensions, coordinating work with that of all other trades, and performing work in a safe and satisfactory manner.  Review of shop drawings shall not permit any deviation from Plans and Specifications.  Shop drawings must be accompanied by signed statement from contractor, stating that he has reviewed the submittal and that the shop drawings are in compliance with Plans and Specifications.

1.09	PRODUCT OPTIONS AND SUBSTITUTIONS:

A.	Refer to the Instructions to Bidders, Specification Section IB, for requirements in selecting products and requesting substitutions.

B.	Any item not specified herein but submitted for approval as a substitute for the specified item shall be accompanied by manufacturer’s documentation stating/illustrating the following applicable information in addition to the specific information requested in other sections:

- Dimensions/weight.

- Electrical ratings-voltage, amperage, short circuit capability, etc.

- Construction - gauge of steel/aluminum, paint finish/application method, color NEMA type, etc.

- Warranty.

- Local manufacturer’s representative or nearest stocking distributor.

- Length of time the product has been available to the public.

      - SHUTDOWNS

        - Prior to taking any electrical equipment out of service, including non-energized equipment connected to emergency systems, Contractor shall fully coordinate such shutdowns with the facility.

        - Contractor shall assist the facility in determining the equipment / areas impacted by a shutdown by providing labor to trace conduits, feeders and circuits as required.

        - All shutdowns must be coordinated with the facility a minimum of seven days in advance.  The facility reserves the right to delay a shutdown if necessary for a full understanding of the impacted areas and / or for making necessary arrangements to minimize impact of the shutdown to facility operations.  Any facility delays associated with a shutdown shall not be a cause for time extensions to the contract or changes to the completion date.  For this reason, the Contractor is strongly encouraged to provide more than the minimum-required seven days advance notice.

      - SITE VISIT

        - Prior to bidding, Contractor shall visit the site to thoroughly review the scope of work and observe existing conditions.  The Contractor shall be familiar with the scope identified on the drawings prior to visiting the site and shall become familiar with existing field conditions impacting the scope of work, including, but not limited to, the following:

          - Location of control and power sources relative to the location of new devices and equipment.

          - Location of existing devices to be removed within the areas of work.

          - Structural conditions such as locations of masonry walls, beams, etc.

          - Modifications required to existing equipment to accomplish the work.

          - Requirements set forth by the Quality Assurance Standards that are not clearly identified on the drawings.

          - Existing equipment, devices, conduit, etc. that must be relocated in order to accomplish the work.  This shall apply to conditions that are visually apparent in the field without the need for selective demolition.

        - Additional compensation will not be considered for additional work required by the Contractor as a result of the Contractor's failure to comply with this requirement.

        - Any items discovered that require additional work not clearly identified by the drawings shall be brought to the immediate attention of the Engineer prior to bid for issuance of an Addendum.

      - LOAD MEASUREMENTS

        - Where new branch circuits or feeders are added to existing distribution equipment, Contractor shall take load measurements in accordance with NFPA 70: 220.87 (1), Exception.  Load measurement readings shall be delivered to the Engineer for verification of existing distribution equipment sizes.  Electrical rough-ins for new circuits and feeders shall not begin until existing distribution equipment capacities are verified by the Engineer.

        - Prior to adding new fixtures, devices, etc. to existing branch circuits, Contractor shall measure existing circuit loads to confirm available capacity.  Contractor shall report values to the engineers for confirmation.

      - WIRING FOR EQUIPMENT BY OTHERS:

        - Under other divisions of work, equipment will be furnished (such as motors, motor drives, and magnetic motor starters).  Connection/interconnection of that equipment shall be part of DIVISION 16.

      - TESTING AND COMMISSIONING

        - The contractor shall conduct tests to demonstrate that the electrical systems are installed and will operate properly and in accordance with the requirements of this Project Manual.  Tests shall be performed in the presence of the Engineer.

        - The Contractor shall furnish all instruments and personnel required for testing.  Instruments used for testing shall have been calibrated within 6 months of the test date.  Contractor shall furnish calibration certificate to the Engineer upon request.

        - Any work, equipment, devices, fixtures, systems, or materials tested and found varying from the requirements of the Drawings and Project Manual shall be replaced by the Contractor without additional cost to the Owner.

        - The Contractor shall be responsible for developing and implementing a test plan for all major electrical equipment installed, including any equipment that is Owner-furnished.  Test plans shall be submitted to the Engineer for review at least 2 weeks in advance of performing the tests.  At a minimum, the plan shall identify the equipment to be tested, the test to be performed, the intended result of the test, and any impact to hospital operations (required shut-downs, etc.).

        - Whether or not specifically identified in this project manual, the Contractor shall provide all examinations, inspections, tests, calibrations, programming, start-up, and commissioning required by the manufacturer’s published instructions and by applicable published NFPA standards.  Contractor shall document the results of tests, inspections, etc. and shall make results available to the Engineer for review upon request.

        - Contractor shall be responsible for demonstrating that the installed systems, equipment, fixtures, devices, etc. are fully functional and without deficiencies.

        - The requirements of this section shall be in addition to any and all specific tests which may be called for in other sections, such as high-potential tests, meggar test, phasing tests, etc.

1.15	DELIVERY, STORAGE AND HANDLING:

A.	Deliver products to project properly identified with names, model numbers, types, grades, compliance labels, and similar information needed for distinct identifications, adequately packaged and protected to prevent during shipment, storage, and handling.

B.	Store equipment and materials at the site, unless offsite storage is authorized in writing.  Protect stored equipment and materials from damage according to manufacturer’s instructions.

C.	Coordinate deliveries of electrical materials and equipment to minimize construction site congestion.

1.16	RECORD DOCUMENTS:

A.	Include the following information:

- Description of function, normal operating characteristics and limitations, performance curves engineering data and tests, and complete nomenclature and commercial numbers of all replaceable parts.

- Manufacturer’s printed operating procedures to include start-up, break-in, routine and normal operating instructions; regulation, control, stopping, shutdown, and emergency instructions; and summer and winter operating instructions.

- Maintenance procedures for routine preventative maintenance and troubleshooting; disassembly, repair, and reassembly; aligning and adjusting instructions.

- Servicing instructions and lubrication charts and schedules.

1.17	WARRANTIES:

A.	Compile and assemble the warranties specified in Division 16, into a separated set of vinyl covered, three ring binders, tabulated and indexed for easy reference.

B.	Provide complete warranty information for each item to include product or equipment to include date of beginning of warranty or bond; duration of warranty or bond; and names, addresses, and telephone numbers and procedures for filing a claim and obtaining warranty services.

1.18	CLEANING:

A.	Clean and restore to original finish all equipment prior to final acceptance.

1.19	GUARANTEE:

A.	The work installed shall be kept in perfect working order for one year from date of final written acceptance of the project, said guarantee to be based upon defective materials and/or workmanship.  Furnish free of cost to the Owner materials and labor necessary to comply with this guarantee.

1.20	MOUNTING HEIGHTS:

A.	Unless otherwise noted on the Drawings or approved by the Architect/Engineer, the following mounting heights shall apply:

1.	Heights of Outlet boxes - all heights measured from finished floor or working surface to top of box:

- Wall Switches	48”

- Receptacle Outlet	54”

2.	The mounting height of disconnect switches, circuit breakers, motor controllers, push button station, and other similar devices and equipment will vary depending upon location and whether individually or group mounted.  For convenience and safety, operating levers, handles or buttons shall be mounted no more than 72” above the finished floor line or working surface.

3.	Individual devices or pieces of equipment, unless otherwise specified, shall be located so that the operating handle, lever or button is located approximately 66” above the finished floor line or working surface.

4.	Panelboards shall be located so that the highest overcurrent protective device is not higher than 72” above the floor or working surface.

5.	Push button stations shall be located 54” above the working surface.

1.21	WORKMANSHIP:

- Install all materials and electrical components of the work in accordance with instructions of manufacturer following the best modern construction practices and conforming with the Contract Documents.  Workmanship shall be first class, in both function and appearance, whether finally concealed or exposed and shall be performed by experienced workmen skilled in the type of work.  As practicable, the lines of all components of the system shall be perpendicular or parallel.  In general, workmanship shall conform to guidelines set for the in N.E.C.A. manuals.

1.22	SAFETY:

A.	It shall be the Contractor’s responsibility to do all things necessary in the pursuit of the installation or testing to provide safe conditions in which to work.

B.	Each Subcontractor shall have an OSHA [29CFR1926.404(b)(1)(iii)] approved equipment grounding conductor program in effect that shall be available for inspection by the Engineer.  480 or 240-volt plugs or cords should not be disconnected or handled without first turning off the switch box power.

C.	Each Subcontractor shall have a lockout, tag-out procedure that complies with OSHA standards.  Tools and equipment that do not comply with OSHA standards shall not be used.  Daily pre-use inspection is required of all tools and equipment.

D.	Scaffolding shall comply with OSHA standards.  Barrels, boxes, cans, spools or other unstable objects shall not be used as work platforms or for the support of planking intended for use as scaffolding.

E.	Subcontractors shall maintain a clean and clear work area at all times.

## END OF SECTION -