# SECTION 16111

RACEWAYS

# PART 1 - GENERAL

1.01	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Special Provisions and Division 1 Specifications sections, apply to work of this section.

B.		This section is a Division 16 Basic Materials and Methods section, and is part of each Division 16 section making reference to electrical raceways specified herein.

PART 2 - PRODUCTS

2.01	METAL CONDUIT AND TUBING:

A.		Rigid Metal Conduit (RMC): Hot-dip galvanized high-strength rigid steel, ¾” taper NPT threads (ANSI B1.20.I) hot galvanized after cutting, conforming to ANSI C80.1 and UL Safety Standard No. 6. Provide zinc coating fused to inside and outside walls.

B.	Liquid-Tight Flexible Metal Conduit (LFMC): Liquid-tight flexible metal conduit; a listed raceway of circular cross-section constructed of a single strip, flexible, continuous, interlocked, and double-wrapped steel; galvanized inside and outside; coated with sunlight-resistant, liquid-tight jacket of flexible polyvinyl chloride (PVC).

C.	Rigid Steel Conduit Fittings:  Malleable iron, UL listed, galvanically compatible with conduit.

2.02	RIGID NONMETALLIC CONDUIT (RNC) AND DUCTS:

- Conduit: RNC - Schedule 80 when un-encased, schedule 40 when encased in concrete, 90 degree C, UL Safety Standard No. 651 rated, constructed of polyvinyl chloride (PVC) and conforming to NEMA TC-2, for direct burial, or encased use, UL-listed and in conformity with UL Safety Standard No. 651 and NEC Article 347.

- PVC Conduit and Tubing Fittings: NEMA Stds. Pub No. TC 3; match to conduit/tubing type and material.

- PVC Utilities Duct Fittings: ANSI NEMA TC 9, match to duct type and material.

- Conduit, Tubing, and Duct Accessories: Provide conduit, tubing and duct accessories of types, sizes and materials, complying with manufacturer’s published product information, which mate and match conduit and tubing

PART 3 - EXECUTION

3.01	INSPECTION:

A.		Examine areas and conditions under which raceways are to be installed, and substrate, which will support raceways.  Notify Engineer in writing of conditions detrimental to proper completion of the work.  Do not proceed with work until unsatisfactory conditions have been corrected in manner acceptable to Architect.

3.02	INSTALLATION OF RACEWAYS:

A.		General:  Install raceways as indicated; in accordance with manufacturer’s written installation instructions, and in compliance with NEC, and NECA’s “Standards of Installation”.  Install units plumb and level, and maintain manufacturer’s recommended clearances.

B.		Coordinate with other work including wires/cables, boxes, and panel work, as necessary to interface installation of electrical raceways and components with other work.

3.03	INSTALLATION OF CONDUITS:

A.		Mechanically fasten together metal conduits, enclosures, and raceways, for enclosing the conductors, to form continuous electrical conductor.  Connect conduits to electrical boxes, fittings and cabinets to provide maximum electrical conductivity and an effective mechanical assembly.  Use nondeteriorating conductive lubricant (Appleton TLC or Crouse Hinds) to make up all conduit threaded joints.

B.		Avoid use of dissimilar metals, except where allowed by NEC, throughout system to eliminate possibility of electrolysis.  Where dissimilar metals are in contact, coat the interface of all dissimilar surfaces with corrosion inhibitor compound before assembly.

C.		Install miscellaneous fittings such as reducers, chase nipples, 3-piece unions, split couplings, and plugs that have been specifically designed and manufactured for their particular application and that are UL listed.  Install expansion fittings in exterior raceways every 100’ linear run or wherever structural expansion joints are crossed.

D.		Use roughing-in dimensions of electrically operated unit furnished by supplier.  Set conduit and boxes for connection to units only after review of dimensions and after checking location with other trades.

E.		Provide nylon pull cord in empty conduits.  Test conduits required to be installed, but left empty, with ball mandrel.  Clear any conduit, which rejects ball mandrel.  Pay costs involved for restoration of conduit and surrounding surfaces to original condition.

F.		Conduit Installation:

- Provide rigid galvanized steel with threaded couplings unless noted otherwise on drawings.

- Use PVC conduit only when encased in concrete, unless otherwise indicated.

G.		Use flexible conduit for final 24” of connection to indoor motors and equipment, or items subject to movement or vibration.

H.		Use liquid-tight flexible conduit where subjected to one or more of the following conditions:

- Moist or humid atmosphere where condensate can be expected to accumulate.

- Corrosive atmosphere.

- Subjected to water spray or dripping oil, water or grease.

I.		Cut conduits straight, properly ream, and cut threads for heavy wall conduit deep and clean.

J.		Field-bend conduit with benders designed for purpose so as not to distort nor vary internal diameter.

K.		Size conduits to meet NEC, except no conduit smaller than ¾ inch shall be embedded in concrete or masonry.

L.		Fasten conduit terminations in NEMA 4X enclosures using Meyers hubs, with grounding bushings.

M.	Conduits are not to cross open concrete basins.

N.		Keep conduits a minimum distance of 6” from parallel runs of flues, hot water pipes or other sources of heat.  Wherever possible, install horizontal raceway runs above water and steam piping, unless noted otherwise.

O.		Running threads at conduit joints and terminations; is prohibited.  Where required, use 3-piece union or split coupling.

P.		Complete installation of electrical raceways before starting installation of cables/wires within raceways.

Q.		Support vertical conduit of any size at a maximum of every 8 feet with clamp hangers.

R.		Concealed conduits of any size, installed in concrete walls, shall be spaced a minimum of 2” from the edge of concrete.

S.		In addition to other conduit support requirements, conduits shall be securely fastened within 12 inches of each box, cabinet, or other conduit termination.

T.		Conduits Underground and below slabs:

- Raceways installed underground shall be rigid schedule 80 PVC, unless indicated otherwise.

- For conduits stubbed-up through slab, all conduit sections installed in the ground and under the slab shall be supported (hung) from slab utilizing 1/4” stainless steel rod and conduit pipe strap every four (4) feet, maximum.

U.		Exposed Conduits:

- Install exposed conduits and extensions from concealed conduit systems neatly, parallel with, or at right angles to walls of building or structure.

- Install exposed conduit work as not to interfere with inserts, lights, pipes or outlets.

- Support exposed conduits by use of hangers, clamps, or clips.  Support conduits on each side of bends and on spacing not to exceed the following 8 feet.

V.		Rigid Non-Metallic Conduits (RNC):

- Non-metallic conduit installed underground shall be installed in concrete envelope as shown on plans, unless indicated otherwise.  Where conduit rises out of ground or enters the building or structure, rigid metal conduit (RMC) shall be used and connected with adapters designed for the purpose.  Ninety-degree elbows shall be rigid galvanized steel.  Concrete envelope shall extend to 6” above grade with edges chamfered 1” at 45 degree where conduit rises out of ground.  To provide added corrosion protection to the RMC at the concrete envelope interface, coat the conduit 12” above and below the interface with a quick-drying, non-sag rubber base primer that permeates the metal surface pits and irregularities and then tape the area with a compatible, corrosion resistant tough PVC tape 20 mils thick having a high-tack adhesive.

- Make solvent-cemented joints in accordance with recommendations of manufacturer.  Use a conduit cleaner fluid, and then make the glued joints.

- Install PVC conduits in accordance with NEC and in compliance with manufacturer’s requirements.

5.	All RNC raceway runs shall have an adequate number of expansion coupling joints with the optimum piston opening and when possible, mount in the horizontal and level position according to manufacturer’s requirements to compensate for temperature variations.  For a vertical run, the expansion coupling must be installed close to the top of the run with the barrel jointing down, in order that rainwater does not run into the opening.  The lower end of the conduit run must be secured at the bottom so that any length change due to temperature variation will result in an upward movement.

6.	Any field bends shall be made using conduit heating and bending equipment manufactured specifically for that purpose.

W.	Install locknuts on conduit entering metal enclosure with the sharp edge of locknut positioned to dig into metal, and wrench tighten outside circumference for proper fastening.

X.		Terminate conduits, smaller than 1-1/4”, with bushings having flared bottom and ribbed sides, with smooth upper edges to prevent injury to cable installation.

Y.		Install insulated type bushing for terminating conduits 1-1/4” and larger.  Bushings shall have flared bottom and ribbed sides.  Upper edge is to have phenolic insulating ring molded into bushing.  Bushing of standard or insulated type shall have screw type grounding terminal.

Z.		Make changes in direction of raceway run with proper fittings, supplied by raceway manufacturer.

## END OF SECTION –