# SECTION 16120

WIRES AND CABLES

# PART 1 - GENERAL

1.01	RELATED DOCUMENTS:

A.		Drawings and general provisions of Contract, including General and Special Provisions and Division 1 Specification sections, apply to work of this section.

B.		This section is a Division 16 Basic Materials and Methods section and is part of each Division 16 section making reference to wires and cables specified herein.

1.02	DESCRIPTION OF WORK:

A.		Extent of electrical wire and electrical cable work is indicated by drawings and schedules.

1.03	QUALITY ASSURANCE:

A.		Manufacturers:  Firms regularly engaged in manufacturer of electrical wire and cable products of types, sizes, and ratings required, whose products have been in satisfactory use in similar service.

B.		Installer’s Qualifications: Firm with successful installation experience with projects utilizing electrical wiring and cabling work similar to that required for this project.

C.		UL Compliance: Comply with applicable requirements of UL Std. 83, “Thermoplastic-Insulated Wires and Cables,” and Std. 486A, “Wire Connectors and Soldering Lugs for Use with Copper Conductors.”

D.		UL Compliance: Provide wiring/cabling and connector products which are UL-listed and labeled.

E.		ETL Compliance: Provide wiring/cabling and connector product, which are ETL-listed and labeled.

F.		NEMA/ICEA Compliance: Comply with NEMA/ICEA Std. Pub. /No.’s WC 5, “Thermoplastic-Insulated Wire and Cable for the Transmission and Distribution of Electrical Energy,” and WC-30, “Color Coding of Wires and Cables,” pertaining to electrical power type wires and cables.

G.		IEEE Compliance: Comply with applicable requirements of IEEE Stds. 82, “Test Procedures for Impulse Voltage Tests on Insulated Conductors,” and Std. 241, “IEEE Recommended Practice for Electrical Power Systems in Commercial Buildings” pertaining to wiring systems.

H.		ASTM Compliance: Comply with applicable requirements of ASTM B1, 2, 3, 8 and D-753.  Provide copper conductors with conductivity of not less than 98% at 20 C (68F).

1.04	DELIVERY, STORAGE, AND HANDLING:

A.		Deliver wire and cable properly packaged in factory-fabricated type containers, or wound on NEMA-specified type wire and cable reels.

B.		Store wire and cable in clean and dry space in original container according to manufacturer’s recommendations.  Protect products from weather, damaging fumes, construction debris and traffic.

C.		Handle wires and cables carefully to avoid abrading, puncturing, and tearing wire and cable insulation and sheathing.  Ensure dielectric resistance integrity of wires/cables is maintained.

D.		Unloading equipment should not come in contact with the cable or its protective covering,

E.		If crane type equipment is used to unload the cable, Contractor shall use a shaft through the arbor hole of the reel or a cradle evenly supporting both reel flanges,

F.		If forklift type equipment is used for unloading, the Contractor shall have the equipment forks to evenly contact both flanges.  Forklift supporting the reel from only one flange in any way shall not be acceptable,

G.		Reel shall be rolled evenly on the ends of both reel flanges,

H.		Reels shall not be rolled off any elevated platform on to the ground,

I.		Multiple cable reels shall not be stacked on top of one another nor shall the reel be allowed to rest on the flat side of one flange, both flanges shall always be used to support the cable reel,

J.		Cable reels shall be stored out of harm’s way to prevent both physical and environmental hazards,

K.		In storage, cable ends shall always be effectively sealed to prevent the entrance of moisture.

PART 2 - PRODUCTS

2.01	WIRE AND CABLE:

A.		General:  Except as otherwise indicated, provide UL-listed wire, cable and connectors of manufacturer’s standard materials, as indicated by published product information, designed and constructed as recommended by manufacturer, and as required for the installation.

2.02	CONDUCTORS UNDER 600V:

A.		Provide factory-fabricated wire of sizes, ratings, materials and types indicated for each service.  Where not indicated, provide proper selection as determined by Installer to comply with project’s installation requirements and NEC standards.  Select from the following types, materials, conductor configuration, insulation and coverings:

- UL Type: THHN/THWN-2.

- Material:  Copper.

- Conductors:  Concentric-lay-stranded (standard flexibility).

2.03	CONNECTORS:

- General:  Provide UL-type, solderless, factory-fabricated, metal connectors of sizes, ampacity ratings, materials, type and classes for applications and services indicated.  Where not indicated, provide proper selection as determined by Installer to comply with project’s installation requirements, NEC and NEMA standards.

B.		For #6 and smaller conductors, use pre-insulated 3M “Scotchlock” thread-on connectors.  For larger conductors, use Kearney or Burndy two-bolt connectors insulated with rubber tape and covered with vinyl plastic electrical tape.  Do not use split-bolt type connectors.

C.		For control wiring terminations, use terminal blocks with 20-ampere, screw-pressure box terminals with insulating barriers and numbered terminals.  Provide ten percent spare terminals with a minimum of two spare terminals.

PART 3 - EXECUTION

3.01	INSPECTION:

A.		General:  Install electrical cables and wires as indicated, in compliance with manufacturer’s written instructions, applicable requirements of NEC and NECA’s “Standard of Installation,” and in accordance with recognized industry practices.

B.		Coordinate cable and wire installation work with electrical raceway and equipment installation work, as necessary for proper interface.

C.		Do not pull conductors into raceways until raceway system (including all outlets, cabinets, bushings and fittings) is completed.  Verify that all work of other trades, which may cause conductor damage, is completed.  Use only approved cable lubricants when necessary.

D.		Pull conductors together where more than one is being installed in a raceway.

E.		Use pulling compound or lubricant, where necessary; compound must not deteriorate conductor or insulation.

F.		Use UL-listed pulling means, including fish tape, cable or rope, which cannot damage raceway.

G.		Use splice and tap connectors which are compatible with conductor material.

H.		The system shall be properly grounded and continuously polarized (phase) throughout.

I.		In general, conductors shall be of the same size from the last protective device to the load.

J.		On termination at branch circuit outlets leave a minimum of eight inches (8”) free conductor for installation of devices and fixtures.

K.		Cover uninsulated splices, joints and free ends of conductor with rubber tape and PVC electrical tape.  Plastic insulating caps may serve as insulation for wire sizes through #6, in combinations listed by the insulating cap manufacturer.

L.		Do not use mechanical means to pull wire No. 8 or smaller.

M.	Branch circuit conductors shall not be smaller than #12 AWG and shall be sized as required by the load served and for specific N.E.C. requirements.

N.		Branch circuit wires, which come within 3” of a ballast within a light fixture, e.g., wires running through end-to-end connected fluorescent fixtures, must be rated for 90C.

O.		Control circuit conductors, unless indicated otherwise, shall be #14 AWG, minimum.

P.		All single conductor cables shall be installed in conduit.

Q.		Grounding conductors shall either have green insulation, or shall have green tape applied at all accessible places.

3.02	FIELD QUALITY CONTROL:

A.		Below 600 Volts:

- General Branch Circuit Wiring.

- Prior to energization, test cables and wire for continuity of circuitry, and also for short circuits.

- Subsequent to wire and cable hook-ups, energize circuitry and demonstrate functioning in accordance with requirements.

- Feeder Circuit Wiring:

a.	Megger test and record results.  Submit results to Engineer for record purposes.

b.	All cable tested above shall read 50 (fifty) megohms or better, at 1000 volts DC, after 60 seconds.  Use 120 volt motorized megger.

## - END SECTION -