# SECTION 16181

OVERCURRENT PROTECTIVE DEVICES

PART 1 - GENERAL

1.01	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Special Provisions and Division 1 Specification sections, apply to work of this section.

B.	This section is a Division 16 Basic Materials and Methods section, and is part of each Division 16 section making reference to overcurrent protective devices specified.

1.02	DESCRIPTION OF WORK:

A.	Extent of overcurrent protective device work is indicated by drawings and schedules.

B.	Types of overcurrent protective devices in this section include the following:

- Circuit breakers (600 volts and below).

- Fuses (600 volts and below).

C.	Refer to other Division 16 sections for cable/wire and connector work required in conjunction with overcurrent protective devices; not work of this section.

PART 2 - PRODUCTS

2.01 	CIRCUIT BREAKERS

A.	General: Except as otherwise indicated, provide circuit breakers of types, sizes, ratings and electrical characteristics indicated, which comply with manufacturer's standard design, materials, components, and construction in accordance with published product information and as required for a complete installation.

D.	Molded-Case Circuit Breakers:

- Provide bolt-on factory-assembled, molded-case circuit breakers of frame size, trip and interrupting rating as shown on the Panel Schedule and Drawings.

- All molded case circuit breakers shall be listed per U.L. 489 to continuously carry 80% of its nameplate rating (unless noted otherwise) and shall meet the requirements of NEMA AB1, and the NEC-NFPA 70.

- Accessories for molded case breakers shall include (when indicated on drawings and schedules) auxiliary switch, shunt trip, under voltage release, bell alarm, motor operator, and mechanical interlocks.

2.02	FUSES:

A.	General: Except as otherwise indicated, provide fuses of types, sizes and ratings and electrical characteristics indicated, which comply with manufacturer's standard design, materials, and construction in accordance with published product information and with industry standards and configurations.

B.	Class RK5 Time-Delay Fuses: Provide UL Class RK5 dual element time-delay fuses, 60 Hz., with 200,000 RMS symmetrical interrupting current rating for protecting motors, transformers, feeders, etc. below 600 amperes.

PART 3 - EXECUTION

3.01 	INSTALLATION OF OVERCURRENT PROTECTIVE DEVICES:

A.	Install overcurrent protective devices as indicated in accordance with the manufacturer's written instructions and with recognized industry practices to ensure that protective devices, especially the rejection feature, comply with requirements. Comply with NEC and NEMA standards for installation of overcurrent protective devices.

B.	Coordinate with other work, including electrical wiring work, necessary to interface installation of overcurrent protective devices with other work.

C.	Fasten circuit breakers without mechanical stresses, twisting or misalignment being exerted by clamps, supports, or cables.

E.	Install fuses in fuse holder with the labeling on the fuse right side up and positioned as that fuse label is readable with the enclosure door open.

F.	Provide spare fuses (3 of each ampere rating used).

G.	For Class R type fuses as specified, the fuse holder shall include the appropriate fuse rejection clip which accepts only Class R fuses.

3.02 	ADJUST AND CLEAN:

A.	Inspect circuit-breaker operating mechanisms for malfunctioning and, where necessary, adjust units for free mechanical movement.

3.03 	FIELD QUALITY CONTROL:

A.	Prior to energization of overcurrent protective devices; test devices for continuity of circuitry and for short-circuits. Correct malfunctioning units, and then demonstrate compliance with requirements.

- END SECTION -