SECTION 16190

SUPPORTING DEVICES

PART 1 - GENERAL

1.01 	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Special Provisions and Division-1 Specification sections, apply to work of this section.

B.	This section is a Division-16 Basic Materials and Methods sections and is a part of each Division-16 section making reference to supports, anchors, sleeves, and seals specified herein.

1.02 	QUALITY ASSURANCE:

A.	NEC Compliance: Comply with NEC as applicable to construction and installation of electrical supporting devices.

B.	ANSI/NEMA Compliance: Comply with applicable requirements of ANSI/NEMA Std. Pub. No. FB 1, “Fittings and Supports for Conduit and Cable Assemblies”.

C.	MSS Compliance: Comply with applicable MSS standard requirements pertaining to fabrication and installation practices for pipe hangers and supports.

D.	NECA Compliance: Comply with National Electrical Contractors Association' s "Standard of Installation:” pertaining to anchors, fasteners, hangers, supports, and equipment mounting.

E.	UL Compliance: Provide electric components, which are UL listed and labeled.

PART 2 - PRODUCTS

2.01 	MANUFACTURED SUPPORTING DEVICES:

A.	General: Provide supporting devices complying with manufacturer’s standard materials, design and construction in accordance with published product information, and as required for a complete installation and as herein specified.  Where more than one type of device meets indicated requirements, selection is Installer’s option.

B.	Manufacturer: Subject to compliance with requirements, provide hot-dip galvanized C-strut of the following, unless otherwise noted on the drawings:

- Power Strut - PS200 series, PS500 series

- Unistrut Div. - P1000 series, P4100 series

- B-Line - B22 series, B54 series

C.	Unistrut channel, conduit straps, and bolts and nuts shall be hot-dip galvanized steel for steel conduit.  Hanger rods, beam clamps, concrete inserts and miscellaneous hardware shall be hot-dip galvanized.

D.	Hardware: All hardware items which are not part of manufactured equipment and which are supplied by the Contractor shall be hot-dip galvanized steel for use with galvanized materials or equipment. Cadmium plated hardware willl not be allowed.

PART 3 - EXECUTION

3.01 	INSTALLATION OF SUPPORTING DEVICES:

A.	Install supports as indicated, in accordance with manufacturer's written instructions, and with recognized industry practices to insure supporting devices comply with requirements.  Comply with requirements of NECA, NEC and ANSI/NEMA for installation of supporting devices.

B.	Coordinate with other electrical work, including raceway and wiring work, as necessary to interface installation of supporting devices with other work.

C.	All equipment shall be mounted on or suspended from foundations and supports as specified herein and/or as required on the electrical drawings.

D.	Furnish all steel angles, channels and other materials necessary for the proper support and erection of motor starters, disconnects, panelboards, cabinets, data gathering panels, transformers and any other electrical equipment and/or materials.

E.	Panelboards, disconnects, cabinets, large pull boxes, cable support boxes and starters shall be secured to structure and not supported from conduits.  Small panelboards, etc., as approved by Engineer, may be supported on walls. Racks for support of conduit and heavy electrical equipment shall be secured to building construction by substantial structural supports.

F.	Supports for conduit shall consist of malleable iron conduit clamps of an approved type, conduit hangers, pipe hangers designed for attachment to steel beams, steel c-strut trapeze hanger with all-thread rod hangers, or wall brackets, as required to suit special conditions.

G.	Outlet boxes shall be supported to masonry or concrete construction by stainless steel expansion anchors and by hot-dip galvanized clamps to steel beams.

H.	Vertical runs in chases and closets shall be supported at intervals not exceeding 8 feet in diameter.

I.	Hangers for conduit shall be supported from the building structural members. Exposed rigid conduit shall be supported every 8 feet and within 12 inches of each outlet box, junction box, cabinet or fitting, unless indicated otherwise.

J.	Supports for horizontal conduits shall be spaced not more than 8-feet apart, unless indicated otherwise, with not less than two supports for each 10-foot straight length and one support near each elbow or bend.

- END SECTION -