SECTION 16441

ENCLOSED SWITCHES

# PART 1 - GENERAL

1.01 	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Special Provisions and Divisions 1 Specification sections, apply to work of this section.

B.	This section is a Division 16 Basic Materials and Methods section, and is part of each Division 16 section-making reference to motor and circuit disconnect switches specified herein.

1.02	DESCRIPTION OF WORK:

A.	Types of circuit disconnect switch work is indicated by drawings and schedules.

1.03	QUALITY ASSURANCE:

A.	UL Compliance:  Comply with requirements of UL 98, “Enclosed and Dead-Front Switches”.  Provide circuit and motor disconnect switches which have been UL-listed and labeled.

B.	NEMA Compliance:  Comply with applicable requirements of NEMA Stds. Pub. No. KS 1, “Enclosed Switches” and 250, “Enclosures for Electrical Equipment (1000 Volts Maximum).

## PART 2  -  PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS:

A.	Heavy-Duty Safety Switches:  Provide surface-mounted, heavy-duty type sheet-steel enclosed safety switches, of types, sizes and electrical characteristics indicated, horsepower rated, solid neutral, incorporating quick-make, quick-break type switches; constructed that blades are visible in OFF position with door open.  Provide equipment with operating handle which is integral part of enclosure and whose position is easily recognizable, and is padlockable in the OFF position; construct current carrying parts of high-conductivity copper, with silver-tungsten type switch contacts, and positive pressure type reinforced fuse clips.

C.	All fusible switches shall accept only Class R fuses, and shall have U.L. listed Class R fuse rejection clips.

D.	The U.L. short circuit rating shall be 200,000 RMS symmetrical amperes when Class R fuses are used.

E.	All switches shall be U.L. listed for use with copper or aluminum wire whose ampacity and temperature rating are in compliance with NEC 110-14(C).

## PART 3  -  EXECUTION

3.01	INSTALLATION OF CIRCUIT DISCONNECT SWITCHES:

A.	Install disconnect switches where indicated, complying with manufacturer’s written instructions, applicable requirements of NEC, NEMA, and NECA’s “Standard of Installation”, and in accordance with recognized industry practices to ensure that products fulfill requirements.

B.	Coordinate circuit disconnect switch installation work with electrical raceway and cable work, as necessary for proper interface.

C.	Install disconnect switches used for motor-driven appliances, and motors and controllers within sight of controller position unless otherwise indicated.

D.	Provide and install fuses where applicable.  Fuse shall be mounted right side up, so its label can be read left to right or bottom to top when the enclosure door is open.

E.	Vacuum clean debris from all enclosures.

3.02	GROUNDING:

A.	Provide equipment grounding connections, sufficiently tight to assure a permanent and effective ground, for electrical disconnect switches where indicated.

3.03	FIELD QUALITY CONTROL:

A.	Subsequent to completion of installation of electrical disconnect switches, energize circuitry and demonstrate capability and compliance with requirements.  Where possible, correct malfunctioning units at project site, then retest to demonstrate compliance; otherwise remove and replace with new units and retest.

### END SECTION -